BILCO Type LV automatic smoke vents provide the security a smoke vent with the added benefits of a skylight. The Lumivent® features a multi-wall polycarbonate cover design that resists UV degradation and offers superior insulation performance over traditional domes. Vents are available in aluminum construction and in a number of UL-Listed standard sizes. For more information, please visit our website www.bilco.com or call 1-800-366-6530.

SECTION 077236

AUTOMATIC SMOKE VENTS

(BILCO TYPE LV)

GENERAL

SUMMARY

Work Included:  Provide factory-fabricated double-leaf automatic smoke vents.

SUBMITTALS

Product Data:  Submit manufacturer’s product data.

Shop Drawings: Submit shop drawings including profiles, accessories, location, fusible links, adjacent construction interface, and dimensions.

Warranty:  Submit executed copy of manufacturer’s standard warranty.

QUALITY ASSURANCE

Manufacturer:  A minimum of 5 years experience manufacturing similar products.

Installer:  A minimum of 2 years experience installing similar products.

Manufacturer’s Quality System: Registered to ISO 9001 Quality Standards including in-house engineering for product design activities.

DELIVERY, STORAGE AND HANDLING

Deliver products in manufacturer’s original packaging. Store materials in a dry, protected, well-vented area. Inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

WARRANTY

Manufacturer’s Warranty:  Provide manufacturer’s standard warranty.  Materials shall be free of defects in material and workmanship for a period of five years from the date of purchase. Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge.

PRODUCTS

manufacturer

Basis-of-Design Manufacturer:  Type LV Lumivent, Translucent Automatic Roof Fire Vent by The BILCO Company, P.O. Box 1203, New Haven, CT 06505, 1-800-366-6530, Fax: 1-203-535-1582, Web: www.bilco.com.

AUTOMATIC ROOF FIRE VENT

Furnish and install where indicated on plans metal fire vent Type LV, size [insert: width (______) x length (______)]. Length denotes hinge side. The roof fire vent shall be double leaf. The roof fire vent shall be preassembled from the manufacturer.

Performance characteristics:

Vent(s) shall be UL listed.

Covers shall be reinforced to support a minimum live load of 40 psf (195kg/m2) with a maximum deflection of 1/150th of the span.

Lifting mechanism assemblies shall open the vent covers simultaneously when latch is manually released or when heat breaks the UL listed fusible link. Opening shall be in a controlled manner to avoid damage to surrounding roof surfaces.

Entire roof fire vent shall be weather tight.

Latch mechanisms shall hold the covers in the closed position without overstressing the fusible link and withstand 40 psf (195kg/m2) wind uplift forces acting on the cover.

Latch operation: When heat parts the UL listed fusible link, the latch shall release instantaneously, allowing vent covers to open. The latch shall be designed for easy resetting, after a fire or test, so that the covers cannot be latched closed unless the mechanism has been reset properly. Manufacturer shall provide instructions for resetting the latch with each unit.

Covers: Shall be constructed with a translucent multi-wall polycarbonate sheet framed with rigid extruded aluminum and coated for UV resistance.  Glazing shall provide an R-factor of 2.38 (U=2.39W/m2K) per ASTMD236.  Covers shall slope 4:12 per Section 2610.3 of IBC (ICC).

Curb: Shall be 12" (305mm) in height and of 11 gauge (2.3mm) aluminum, pitched 20° to a fixed center channel. Curb shall be formed with a 3-1/2" (89mm) flange with 7/16" (11mm) holes provided for securing to roof deck. Curb shall be equipped with an integral 11 gauge (2.3mm) aluminum capflashing and feature the Bil-Clip® flashing system, including stamped tabs, 6" (153mm) on center, to be bent inward to hold single-ply roofing membrane securely in place.  Curb shall have a dual-durometer co-extruded EPDM rubber gasket that is mechanically fastened to the top of the curb to assure a continuous seal when compressed against the underside of the cover.

Curb insulation: Shall be rigid, high-density fiberboard of 1" (25mm) thickness on the outside of curb.

Lifting mechanisms: Manufacturer shall provide high performance gas springs which apply forces to the center of the cover and open the covers in a controlled manner against 10 lb/ft2 (49Kg/m2)] snow/wind load. Gas springs shall have a cyclic durability of 50,000 cycles and have a corrosion resistant outer tube and inner rod.

Latch mechanism: Shall be the BILCO Thermolatch® II positive hold/release mechanism with a separate latching point for each cover controlled by a single UL listed 165°F (74°C) fusible link. Fusible link shall be curb mounted on a non-hinged end to allow the latching mechanism to be easily reset from the roof level.

Hardware

Heavy duty Type 316 stainless steel pintle hinges.

Covers shall automatically lock in the open position with a rigid hold open arm equipped with a 1" (25mm) diameter red vinyl grip handle to permit easy release for closing.

All hardware (unless specified otherwise) shall be zinc plated and chromate sealed. Cover hardware shall be bolted into heavy gauge channel reinforcing welded to the underside of the cover.

Manual pull release cables: Interior and exterior cables with red vinyl grips shall be provided and allow the unit to be opened without disturbing the fusible link.

Finishes: Factory finish shall be mill finish aluminum.

EXECUTION

EXAMINATION

Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.  Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work.

Test units for proper function and adjust until proper operation is achieved.

Test fusible link and install replacement fusible link after testing.

Repair finishes damaged during installation.

Restore finishes so no evidence remains of corrective work.

ADJUSTING AND CLEANING

Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

END OF SECTION