- SECTION 03 62 13

MasterFlow 713 (Formerly Masterflow 713 Plus) Non-Metallic, Non-Shrink Grouting

Notes to specifiers:

Please update your Master Specifications to reflect the company and product name changes. The old product names are provided in parentheses following the new names in this Section for reference.

The purpose of this guide specification is to assist the specifier in developing a project specification for the use of master buidlers solutions products.  this guide document has been prepared to be part of a complete project manual.  it is not intended to be a “stand alone” document, and it is not intended to be copied directly into a project manual.

This guide specification will need to be carefully reviewed for APPROPRIATENESS for the given project and edited accordingly to comply with project-specific requirements.

  - GENERAL

    - SECTION INCLUDES

      - Non-shrink grout.

    - RELATED REQUIREMENTS

Specifier Notes:  Edit the following list of related sections as necessary.  Limit the list to sections with specific information that the reader might expect to find in this section, but is specified elsewhere.

      - Section 03 61 00 – Cementitious Grouting.

    - REFERENCE STANDARDS

Specifier Notes:  List reference standards used elsewhere in this section, complete with designations and titles.

      - ASTM C 109 / C 109M – Standard Test Method for Compressive Strength of Hydraulic Cement Mortars (Using 2-in. or [50-mm] Cube Specimens).

      - ASTM C 939 – Standard Test Method for Flow of Grout for Preplaced-Aggregate Concrete (Flow Cone Method).

      - ASTM C 942 – Standard Test Method for Compressive Strength of Grouts for Preplaced-Aggregate Concrete in the Laboratory.

      - ASTM C 1107 / C 1107M – Standard Specification for Packaged Dry, Hydraulic-Cement Grout (Nonshrink).

      - ASTM C 1315 – Standard Specification for Liquid Membrane-Forming Compounds Having Special Properties for Curing and Sealing Concrete.

      - ASTM C 1602 / C 1602M – Standard Specification for Mixing Water Used in the Production of Hydraulic Cement Concrete.

      - COE CRD-C621 – Specification for Nonshrink Grout.

      - ICRI 310.2 – Selecting and Specifying Concrete Surface Preparation for Sealers, Coatings, and Polymer Overlays.

      - ISO 9001:2008 – Quality Management Systems – Requirements.

    - PREAPPLICATION MEETINGS

Specifier Notes:  Include a preapplication meeting for critical or large projects.  Edit as necessary.  Delete if not needed.

      - Convene preapplication meeting [1 week]  [2 weeks] before start of application of non-shrink grout.

      - Require attendance of parties directly affecting work of this section, including Contractor, Architect, Engineer, applicator, and manufacturer’s representative.

      - Review materials, surface preparation, forming, mixing, placing, curing, protection, and coordination with other work.

    - SUBMITTALS

Specifier Notes:  Edit submittal requirements as necessary.  Delete submittals not required.

      - Comply with Section 01 33 00 – Submittal Procedures.

      - Product Data:  Submit manufacturer’s product data, including surface preparation, forming, mixing, placing, and curing instructions.

      - Manufacturer’s Certification:  Submit manufacturer’s certification that materials comply with specified requirements and are suitable for intended application.

      - Manufacturer’s Project References:  Submit manufacturer’s list of successfully completed non-shrink grout projects, including project name and location, name of architect or engineer, and type and quantity of non-shrink grout furnished.

      - Applicator’s Project References:  Submit applicator’s list of successfully completed non-shrink grout projects, including project name and location, name of architect or engineer, and type and quantity of non-shrink grout placed.

    - QUALITY ASSURANCE

      - Manufacturer’s Qualifications:

        - Manufacturer regularly engaged, for past 15 years, in manufacture of non-shrink grout of similar type to that specified.

        - ISO 9001:2008 certified.

      - Applicator’s Qualifications:

        - Applicator regularly engaged, for past 5 years, in application of non-shrink grout of similar type to that specified.

        - Employ persons trained for application of non-shrink grout.

    - DELIVERY, STORAGE, AND HANDLING

      - Delivery Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

      - Storage and Handling Requirements:

        - Store and handle materials in accordance with manufacturer’s instructions.

        - Keep materials in manufacturer’s original, unopened containers and packaging until application.

        - Store materials in clean, dry area indoors.

        - Do not store materials directly on floor.

        - Protect materials during storage, handling, and application to prevent contamination or damage.

  - PRODUCTS

    - MANUFACTURER

    - Subject to compliance with requirements, provide products from the following manufacturer:

Master Builders Solutions

889 Valley Park Drive

Shakopee, MN  55379 USA

Customer Service:  800-433-9517

Technical Service:  800-243-6739

Direct Phone:  952-496-6000

Website: www.master-builders-solutions.com/en-us

    - Substitutions:  Not permitted.

    - NON-SHRINK GROUT

      - Non-Shrink Grout: “MasterFlow 713” (formerly “Masterflow 713 Plus”).

        - Description:  1-component, high-precision, non-shrink, hydraulic cement-based, graded mineral-aggregate grout.

        - Compliance:

          - ASTM C 1107.

          - CRD-C621, Grades B and C.

        - VOC Content: 0 lbs per gal (g/L).

      - Physical Properties Test Data:

        - Compressive Strength, ASTM C 942, according to ASTM C 1107:

          - 1 Day:

            - Plastic Consistency:  3,400 psi (23 MPa).

            - Flowable Consistency:  3,200 psi (22 MPa).

            - Fluid Consistency:  1,000 psi (7 MPa).

          - 3 Days:

            - Plastic Consistency:  5,500 psi (38 MPa).

            - Flowable Consistency:  4,800 psi (33 MPa).

            - Fluid Consistency:  3,200 psi (22 MPa).

          - 7 Days:

            - Plastic Consistency:  7,000 psi (48 MPa).

            - Flowable Consistency:  6,500 psi (45 MPa).

            - Fluid Consistency:  4,500 psi (31 MPa).

          - 28 Days:

            - Plastic Consistency:  8,500 psi (59 MPa).

            - Flowable Consistency:  7,500 psi (52 MPa).

            - Fluid Consistency:  7,000 psi (48 MPa).

      - Mixing Water:  Potable or ASTM C 1602-compliant water.

      - Membrane Curing Compound:  ASTM C 1315.

  - EXECUTION

    - EXAMINATION

      - Examine areas to receive non-shrink grout.

      - Notify Architect of conditions that would adversely affect surface preparation or application.

      - Do not begin surface preparation or application until unacceptable conditions are corrected.

    - SURFACE PREPARATION

      - Prepare surfaces in accordance with manufacturer’s instructions.

      - Clean steel surfaces to be free of dirt, dust, oil, grease, and other contaminants.

      - Concrete Surfaces to be Grouted:

        - Existing Concrete:  Clean, saturated surface-dry (SSD), sound, and roughened to CSP of 5 to 9 in accordance with ICRI 310.2 to permit proper bond.

        - Freshly Placed Concrete:  Achieve required surface profile in accordance with manufacturer’s instructions.

        - When Dynamic, Shear, or Tensile Forces are Anticipated:

          - Roughness of plus or minus 3/8 inch (10 mm) in accordance with manufacturer’s instructions.

          - Verify absence of bruising in accordance with ICRI 310.2.

      - Saturate concrete surfaces with clean water for 24 hours just before grouting.

      - Remove freestanding water from foundation and bolt holes immediately before grouting.

      - Grout anchor-bolt holes and allow to sufficiently set before major portion of non-shrink grout is placed.

      - Shade foundation from sunlight for 24 hours before grouting.

    - FORMING

      - Build forms for non-shrink grout in accordance with manufacturer’s instructions.

      - Build forms to be liquid tight and nonabsorbent.

    - MIXING

      - Add water to non-shrink grout and mix in accordance with manufacturer’s instructions.

      - Use minimum amount of water required to achieve necessary placement consistency.

      - Do not use mixing water in amount or at temperature that will produce flow of less than 25 seconds in accordance with ASTM C 939 or cause mixed grout to bleed or segregate.

      - Do not retemper non-shrink grout by adding water.

      - Do not add plasticizers, accelerators, retarders, or other additives to non-shrink grout, unless approved by manufacturer.

      - Store and mix non-shrink grout to produce mixed-grout temperature in accordance with manufacturer’s instructions.

    - PLACING

      - Place non-shrink grout in accordance with manufacturer’s instructions at locations indicated on the Drawings.

      - Place non-shrink grout in continuous pour.

      - Place non-shrink grout to prevent entrapment of air or water beneath equipment.

      - Ensure non-shrink grout fills entire space being grouted and remains in contact with plate throughout entire grouting process.

      - Discard grout that becomes unworkable.

      - Do not vibrate grout.

      - Trim non-shrink grout surfaces immediately after placement and cover exposed grout with clean wet rags.  Keep rags wet for 5 to 6 hours.

      - Placement Depth:

        - Minimum:  1 inch (25 mm).

        - Lifts over 6 Inches (152 mm):  In accordance with manufacturer’s instructions.

    - CURING

      - Cure non-shrink grout in accordance with manufacturer’s instructions.

      - Cure exposed non-shrink grout with membrane curing compound immediately after wet rags are removed, to minimize potential moisture loss within grout.

      - Shade foundation from sunlight for 24 hours after grouting.

      - Ensure foundation, plate, and grout temperatures do not fall below 50 degrees F (10 degrees C) until after final set, when grouting at minimum temperatures.

      - Protect non-shrink grout from freezing until it has attained compressive strength of 3,000 psi (20.7 MPa) in accordance with ASTM C 109.

    - PROTECTION

      - Protect placed non-shrink grout from damage during construction.

END OF SECTION

Disclaimer

THIS INFORMATION AND ALL FURTHER TECHNICAL ADVICE ARE BASED ON master builders solutions PRESENT KNOWLEDGE AND EXPERIENCE. HOWEVER, master builders solutions ASSUMES NO LIABILITY FOR PROVIDING SUCH INFORMATION AND ADVICE INCLUDING THE EXTENT TO WHICH SUCH INFORMATION AND ADVICE MAY RELATE TO EXISTING THIRD-PARTY INTELLECTUAL PROPERTY RIGHTS, ESPECIALLY PATENT RIGHTS. IN PARTICULAR, master builders solutions DISCLAIMS ALL CONDITIONS AND WARRANTIES, WHETHER EXPRESS OR IMPLIED, INCLUDING THE IMPLIED WARRANTIES OF FITNESS FOR A PARTICULAR PURPOSE OR MERCHANTABILITY. master builders solutions SHALL NOT BE RESPONSIBLE FOR CONSEQUENTIAL, INDIRECT OR INCIDENTAL DAMAGES (INCLUDING LOSS OF PROFITS) OF ANY KIND. master builders solutions RESERVES THE RIGHT TO MAKE CHANGES ACCORDING TO TECHNoLOGY PROGRESS OR FUrTHER DEVELOPMENTS. IT IS THE CUSTOMERS RESPONSIBILITY AND OBLIGATION TO CAREFULLY INSPECT AND TEST ANY INCOMING GOODS. PERForMANCE OF THE PRODUCT(S) DESCRIBED HEREIN SHOULD BE VERIFIED BY TESTING AND CARRIED OUT ONLY BY QUALIFIED EXPERTS. IT IS THE SOLE RESPONSIBILITY OF THE CUSTOMER TO CARRY OUT AND ARRANGE FOR ANY SUCH TESTING. REFERENCE TO TRADE NAMES USED BY OTHER COMPANIES IS NEITHER A RECOMMENDATION, NOR AN ENDORSeMENT OF ANY PRODUCT AND DOES NOT IMPLY THAT SIMILAR PRODUCT COULD OR COULD NOT BE USED.