GUIDE SPECIFICATION FOR CG-86™:  NON-SHRINK, NON-METALLIC, MINERAL-AGGREGATE BASED GROUT

SECTION 03 62 13

NON-METALLIC, NON-SHRINK GROUTING

Revision Date:  November 13, 2023

Specifier Notes: This guide specification is written according to the Construction Specifications Institute (CSI) MasterFormat. The section must be carefully reviewed and edited by the architect or engineer to meet the requirements of the project. Coordinate this section with other specification sections and the drawings.

Specifier Notes: W. R. MEADOWS® CG-86 construction-grade grout is a non-metallic, mineral aggregate based, non-shrink economical grout. The product is specifically developed as a high-strength, cost-effective, general-purpose grout for use across a broad range of large and small construction projects. CG-86 will not rust and contains no added chlorides or gypsum. CG-86 provides a range of consistency from dry pack to fluid to meet many different application requirements. It is furnished pre-mixed and ready to use. CG-86 may be extended for deep grouting with pea gravel for greater yield and increased economy. CG-86 is freeze-thaw stable and may be used for interior or exterior applications, above- or below-grade. CG-86 is versatile and designed for structural grouting of machine and column baseplate, anchoring, doweling, precast wall panels, and bridge seats and bearing pads. CG-86 is suitable for the transportation, industrial, commercial, and municipal markets.

PART 1		GENERAL

1.01	SECTION INCLUDES

A.	Surface preparation

B.	Application of a non-metallic, non-shrink, cementitious grout.

1.02	RELATED SECTIONS

Specifier Notes: Edit the list of related sections as required for the project. List other sections dealing with work directly related to this section.

A.	Section 03 30 00 – Cast-In-Place Concrete.

B.	Section 03 41 00 – Precast Structural Concrete.

C.	Section 05 12 00 – Structural Metal Framing.

1.03	REFERENCES

A.	ACI 351.1R:  Grouting Between Foundations and Bases for Support of Equipment and Machinery.

B.	ASTM C109:  Standard Test Method for Compressive Strength of Hydraulic Cement Mortars.

C.	ASTM C191:  Standard Test Methods for Time of Setting of Hydraulic Cement by Vicat Needle.

D.	ASTM C230:  Standard Specification for Flow Table for Use in Tests of Hydraulic Cement.

### E.	ASTM C666:  Standard Test Method for Resistance of Concrete to Rapid Freezing and Thawing.

### F.	ASTM C827:  Standard Test Method for Change in Height at Early Ages of Cylindrical Specimens of Cementitious Mixtures.

### G.	ASTM C882:  Standard Test Method for Bond Strength of Epoxy-Resin Systems Used With Concrete By Slant Shear

### H.	ASTM C939:  Standard Test Method for Flow of Grout for Preplaced-Aggregate Concrete (Flow Cone Method)

### I.	ASTM C1107:  Standard Specification for Packaged Dry, Hydraulic-Cement Grout (Nonshrink).

1.04	SUBMITTALS

A.	Comply with Section 01 33 00 - Submittal Procedures.

B.	Submit manufacturer's product data and application instructions.

1.05	DELIVERY, STORAGE, AND HANDLING

A.	Deliver materials to site in manufacturer's original, unopened packaging, with labels clearly identifying product name and manufacturer.

B.	Store materials in a clean, dry area in accordance with manufacturer's instructions.

C.		Protect materials during handling and application to prevent damage or contamination.

1.06	ENVIRONMENTAL REQUIREMENTS

A.	Ensure that substrate ambient air and surface temperatures are 40o F (5o C) within 24 hours of placement.

B.	Do not apply if rain is imminent.

C.	Protect from conditions that may cause early water loss: high winds, low humidity, high temperature, direct sunlight.

D.	Grout will set faster at higher temperatures and slower at lower temperatures.

E.	Follow manufacturer’s recommendations regarding additional installation information (Standard on Hot Weather Concreting, ACI 305-R89 or Standard on Cold Weather Concreting”, ACI 306-R88).

PART 2		PRODUCTS

2.01	MANUFACTURER

A.	W. R. MEADOWS, INC., PO Box 338, Hampshire, Illinois 60140-0338. (800) 342-5976. (847) 683-4500. Fax (847) 683-4544. Website: www.wrmeadows.com.

2.02	MATERIALS

A.	Performance Based Specification:  Cementitious grout shall be non-shrink, non-metallic, and non-corrosive, and shall possess the following properties for plastic consistency:

1.	Compressive Strength, ASTM C109:	24-hour, 3,500 psi (24.1 MPa)

3-day, 4,500 psi (31 MPa)

7-day, 6,000 psi (41.3 MPa)

28-day, 8,000 psi (55.1 MPa)

2.	Set Time, ASTM C191:	4-6 hours.

3.	Flow, ASTM C230:  100-120%.

4.	Bond Strength, ASTM C882:  2,300 psi (15.8 MPa).

5.	Freeze/Thaw Resistance, ASTM C666:  100% Relative Dynamic Modulus.

B.	Proprietary Based Specification:

1.	CG-86 Construction Grout by W. R. MEADOWS, INC.

2.03	ACCESSORIES

.1	Concrete Curing Compound:  1130-CLEAR CURING COMPOUND or 2200-WHITE PIGMENTED CURING COMPOUND or VOCOMP®-20 CURING AND SEALING COMPOUND.

PART 3		EXECUTION

3.01	EXAMINATION

A.	Examine surfaces to receive grout.  Notify engineer if surfaces are not acceptable. Do not begin surface preparation or application until unacceptable conditions have been corrected.

B.	Grouting application shall be performed in accordance with ACI 351.1R.

3.02	SURFACE PREPARATION

A.	Prepare concrete substrate in accordance with ICRI Technical Guideline No 310.2-1997: Specifying Concrete Surface Preparation for Sealers, Coatings, and Polymer Overlays.

B.	Mechanically roughen or high pressure water-jet the existing concrete substrate to an ICRI concrete surface profile (CSP) of CSP-4 or higher.

C.	Remove all unsound concrete and provide a profiled, porous surface that is structurally sound, dust-free, and free of any surface contaminants that will adversely affect the bond.

D.	Wet the substrate to a fully saturated, surface dry (SSD) condition, free of standing water during the entire application of the grout.

E.	Abrasive blast the steel base-plates or any steel that will come in contact with the grout to a white metal finish.

3.03	MIXING

A.	Comply with grout manufacturer’s recommendations for water quantity and mixing procedures based on required consistency.

B.	Mix grout in conventional mortar mixing equipment with rubber blade paddles.

C.	Alternatively, mix grout in appropriate grout pump as recommended by the manufacturer.

D.	Add 2/3 of the amount of water required, then add grout.

E.	Mix grout partially and add the remainder of water for desired consistency.

F.	Mix grout for three minutes or until a lump-free consistency is obtained.

Specifier Notes:  When grouting large areas, extend CG-86 with washed, dried, well-graded, non-reactive, dense pea gravel. For thicknesses 2″ – 4″ (50.8 – 101.6 mm), add up to 25% 3/8″ (9.5 mm) pea gravel. For medium-flow mixes, 4″ (50.8 mm) and over, add up to 50% 3/8″ (9.5 mm) pea gravel.  The addition of pea gravel is based on percentage of the weight of the dry grout.  The use of aggregate to extend the CG-86 will reduce flow and pumping characteristics.  A well graded aggregate conforming to table 2 of ASTM C33, Size Number 8 will help to minimize loss of flow and pumping characteristics.

G.	Mix smaller quantities using a mortar-type mixing paddle and a slow speed drill (400 – 600 RPM) with high torque.

H.	Consult manufacturer’s instructions for deep grouting mixing procedures.

3.04	FORMING

A.	Provide for rapid, continuous, and complete grout placement.

B.	Use forms of sufficient strength, closely fitted with joints sealed to prevent leakage.

C.	Coat forms with a form release.

D.	Provide 1/2” (12.7 mm) minimum form clearance on all sides and 1” (25.4 mm) clearance for 		head.

3.05	PLACEMENT

A.	Place by pouring or pumping using appropriate equipment as recommended by the grout 			manufacturer.

B.	Contact grout manufacturer for details on pumping.

C.	Ensure compaction by rodding or tapping.  Do not vibrate.

D.	Place grout from side or corner to prevent voids and air entrapment.

E.	Alternatively, place excess grout which will be displaced by the weight of the object to be grouted to effect full bearing.

F.	Allow 3” (76 mm) clearance for grout entry and minimum of 6” (152 mm) grout head.

G.	On the opposite side of the entry, allow minimum 1/2” (12.7 mm) clearance between form and equipment and provide initially 1” (25.4 mm) of grout head above the bottom of the equipment base plate.

H.	Reduce all grout heads to 1/8” (3 mm) after initial set.

I.	Provide minimum 1" (25.4 mm) grout thickness between foundation and base plate.

3.06	CURING

A.	Do not remove forms until grout is sufficiently hard to avoid sagging or damaging.

B.	Cure exposed material following placement using wet burlap for 48 hours.

C.	Alternatively cure exposed material using a suitable curing compound.

END OF SECTION